## Input
KE2 Evaporator Efficiency Savings Estimator
Customer:
Job Name:
Location:
Length of walk-in | 15 | Ft
Width of walk-in | 12 | Ft | [10 empty] | Product | Specific Heat above 32 F | Specific Heat below 32F | Freeze Point | Latent Heat of Fusion
Height of walk-in | 8 | Ft | Retrieved Data |  | Evaporators in Space | Insulation |  |  | Utility Rates | Ambient Temp | Ground Temp | US or Canada
Number of glass doors | 1 |  | Ceiling insulation value | 0.72 | 1 | Insulation | Degree Multi. | Alabama | 0.1009 | 95 | 75 | US | Beer | 0.92 | 0.92 | 28 | 129
Temperature of walk-in | -10 | oF | Floor insulation value | 0.72 | 2 | Concrete 6" | 5 | Alaska | 0.1461 | 82 | 40 | US | Dried Fruit | 0.47 | 0.32 | 4 | 29
Type of Defrost | Electric |  | Wall insulation value | 0.72 | 3 | Fiber Glass 4" Thick | 1.44 | Alberta | 0.1 | 95 | 55 | CA | Ice Cream | 0.7 | 0.38 | 21 | 86
Location (adjusts for ambient and utilities) | Alabama |  | Utility Rate | 0.1009 | 4 | Fiber Glass 6" Thick | 0.9 | Arizona | 0.1038 | 105 | 80 | US | Meat | 0.8 | 0.4 | 28 | 105
Floor insulation type | Foamed Urethane 4" Thick |  | Ambient Temp | 95 | Location of Walk-IN | Fiber Glass 8" Thick | 0.72 | Arkansas | 0.0706 | 95 | 70 | US | Milk | 0.93 | 0.49 | 31 | 124
Ceiling insulation type | Foamed Urethane 4" Thick |  | Ground Temp | 75 | Inside | Foamed Urethane 4" Thick | 0.72 | British Columbia | 0.09 | 93 | 70 | CA | Mushrooms | 0.93 | 0.47 | 30.4 | 130
Wall insulation type | Foamed Urethane 4" Thick |  | Air Change over factor | 27 | Outside | Foamed Urethane 6" Thick | 0.48 | California | 0.1657 | 105 | 75 | US | Product Loading Estimate
Type of product | Ice Cream |  | Freeze Point | 21 | Number of Defrost per Day | Polystyrene 4" Thick | 1.44 | Colorado | 0.0959 | 95 | 60 | US | Volume | Cooler (>32) | Freezer (<=32)
Temperature of product entering space | 15 | oF |  |  |  | Polystyrene 6" Thick | 0.9 | Connecticut | 0.1651 | 95 | 65 | US | 0 | 4000 | 1000
Is the walk-in located inside or outside | Outside |  | Calculations |  | 1 | Polystyrene 8" Thick | 0.72 | Delaware | 0.1137 | 95 | 65 | US | 500 | 6200 | 1600
Estimated installation cost (labor & parts) ($US) | 350 |  | Volume of Space | 1440 | 2 |  |  | District of Columbia | 0.1526 | 95 | 65 | US | 3000 | 8000 | 2000
Utilities Rebates ($US) | 0 |  | Product load Calculation | 15200 | 3 | Air Change Over (>32) Heavy |  | Florida | 0.0981 | 95 | 80 | US | 4600 | 11000 | 2500
Estimated annual operating cost ($US) | 5566.9827 |  | Transmission Loads | 60540.48 | 4 | Cu. Ft | air changes | Georgia | 0.0924 | 98 | 75 | US | 8100 | 17000 | 4000
Estimated KW-hr saved annually | 11034.6535 |  | Air Change Load | 135691.2 | 5 | 200 | 88 | Hawaii | 0.2596 | 85 | 80 | US | 12800 | 26000 | 6200
Estimated annual savings ($US) | 1113.3965 |  | Additional Loads (lights Motors, Glass Doors) | 67470 | 6 | 250 | 76 | Idaho | 0.0693 | 95 | 60 | US | 16000 | 33000 | 7500
Estimated Payback For End User | 0.31435 | Yrs | Total BTU LOAD | 278901.68 | Type of Defrost | 300 | 69 | Illinois | 0.0831 | 96 | 60 | US | 20000 | 40000 | 9500
This is an estimating tool for walk-in coolers and freezers with electric or air defrost, mechanical expansion valves 18 hr pull down, & heavy traffic conditions. All systems will vary and your savings may be more or less than the savings generated by this estimator. |  |  | Estimated Annual KW-hr Saved | 11034.6535 | Electric | 400 | 59 | Indiana | 0.0819 | 95 | 60 | US | 28000 | 56000 | 13000
|  |  | Estimated Annual KW-hr Used | 55173.2675 | Air (Off Time) | 500 | 52 | Iowa | 0.0916 | 95 | 60 | US | 40000 | 66000 | 17000
|  |  |  | 0.00054198 |  | 600 | 46 | Kansas | 0.087 | 100 | 60 | US | 60000 | 110000 | 25000
[6 empty] | 800 | 40 | Kentucky | 0.0781 | 95 | 65 | US | 80000 | 150000 | 34000
[6 empty] | 1000 | 35 | Louisiana | 0.0849 | 100 | 75 | US | Heat Removed in cooling air 85F/60RH
[6 empty] | 1500 | 28 | Maine | 0.1218 | 90 | 60 | US | -25 | 3.84
[6 empty] | 2000 | 24 | Manitoba | 0.08 | 95 | 50 | CA | -20 | 3.72
[6 empty] | 3000 | 19 | Maryland | 0.119 | 95 | 65 | US | -15 | 3.6
[6 empty] | 4000 | 16.4 | Massachusetts | 0.1492 | 93 | 65 | US | -10 | 3.49
[6 empty] | 5000 | 14.4 | Michigan | 0.1016 | 95 | 60 | US | -5 | 3.36
[6 empty] | 6000 | 13 | Minnesota | 0.0904 | 92 | 60 | US | 0 | 3.23
[6 empty] | 8000 | 11 | Mississippi | 0.0941 | 95 | 75 | US | 5 | 3.07
[6 empty] | 10000 | 9.8 | Missouri | 0.0885 | 100 | 60 | US | 10 | 2.87
[6 empty] | 15000 | 7.8 | Montana | 0.0855 | 95 | 55 | US | 15 | 2.74
[6 empty] | 20000 | 7 | Nebraska | 0.0829 | 95 | 60 | US | 20 | 2.61
[6 empty] | 25000 | 6 | Nevada | 0.0949 | 95 | 65 | US | 25 | 2.42
[6 empty] | 30000 | 5.4 | New Brunswick | 0.12 | 90 | 60 | CA | 30 | 2.24
[6 empty] | 40000 | 4.6 | New Hampshire | 0.1413 | 90 | 55 | US | 35 | 2.09
[6 empty] | 50000 | 4 | New Jersey | 0.1517 | 95 | 65 | US
[6 empty] | 75000 | 3.2 | New Mexico | 0.0948 | 90 | 65 | US
[6 empty] | 100000 | 2.8 | New York | 0.1788 | 95 | 65 | US
[6 empty] | 150000 | 2.4 | Newfoundland | 0.12 | 93 | 65 | CA
[6 empty] | 200000 | 2.2 | North Carolina | 0.0841 | 95 | 70 | US
[6 empty] | 300000 | 2 | North Dakota | 0.0772 | 95 | 50 | US
[6 empty] | Air Change Over (<32) Heavy |  | Nova Scotia | 0.13 | 90 | 60 | CA
[6 empty] | Cu. Ft | air changes | Ohio | 0.095 | 95 | 65 | US
[6 empty] | 200 | 67 | Oklahoma | 0.0829 | 101 | 65 | US
[6 empty] | 250 | 58 | Ontario | 0.12 | 95 | 60 | CA
[6 empty] | 300 | 52.4 | Oregon | 0.0778 | 90 | 70 | US
[6 empty] | 400 | 45 | Pennsylvania | 0.1032 | 95 | 65 | US
[6 empty] | 500 | 40 | Prince Edward Island | 0.16 | 93 | 65 | CA
[6 empty] | 600 | 36 | Quebec | 0.09 | 95 | 65 | CA
[6 empty] | 800 | 30.6 | Rhode Island | 0.1154 | 93 | 65 | US
[6 empty] | 1000 | 27 | Saskatchewan | 0.1 | 95 | 50 | CA
[6 empty] | 1500 | 22 | South Carolina | 0.0905 | 95 | 75 | US
[6 empty] | 2000 | 18.6 | South Dakota | 0.0801 | 95 | 55 | US
[6 empty] | 3000 | 14.8 | Tennessee | 0.0972 | 95 | 70 | US
[6 empty] | 4000 | 12.6 | Texas | 0.0916 | 100 | 75 | US
[6 empty] | 5000 | 11.2 | Utah | 0.0756 | 95 | 60 | US
[6 empty] | 6000 | 10 | Vermont | 0.1321 | 90 | 60 | US
[6 empty] | 8000 | 8.6 | Virginia | 0.077 | 95 | 70 | US
[6 empty] | 10000 | 7.6 | Washington | 0.0734 | 93 | 70 | US
[6 empty] | 15000 | 6 | West Virginia | 0.0752 | 95 | 65 | US
[6 empty] | 20000 | 5.2 | Wisconsin | 0.1022 | 95 | 55 | US
[6 empty] | 25000 | 4.6 | Wyoming | 0.0763 | 95 | 55 | US
[6 empty] | 30000 | 4.2
[6 empty] | 40000 | 3.6
[6 empty] | 50000 | 3.2
[6 empty] | 75000 | 2.6
[6 empty] | 100000 | 2.2
[6 empty] | 150000 | 2
[6 empty] | 200000 | 1.8
[6 empty] | 300000 | 1.7

## KW-Calc (hidden)
Evaportators
RAE Corp
|  |  | Defrost Heater Amps | Total Fan Motor Amps | BTU Capacity @ Saturated Suction Temperatures | [13 empty] | W-hr/BTU(18 hr runtime, 4 defrost per day, 20 min defrost)
|  | Model | 230/3 | 230/3 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35
| A Series | 410-126 | 10.3 | 1.3 | 11490 | 0.00089643 | 12440 |  | 13190 |  | 13830 |  | 14460 |  | 15170 | 15580 | 16050 | 16580 | 0.041295 |  | 0.038141 |  | 0.035972 |  | 0.034308 |  | 0.032813 |  | 0.031277 | 0.030454 | 0.029562 | 0.028617
|  | 420-338 | 24.9 | 2.6 | 30820 | 0.00080792 | 33370 |  | 35380 |  | 37110 |  | 38800 |  | 40700 | 41800 | 43050 | 44470 | 0.033167 |  | 0.030633 |  | 0.028892 |  | 0.027545 |  | 0.026346 |  | 0.025116 | 0.024455 | 0.023745 | 0.022987
|  | 440-841 | 63.1 | 8 | 76670 | 0.00082301 | 83040 |  | 88040 |  | 92330 |  | 96530 |  | 101260 | 104010 | 107110 | 110640 | 0.03802 |  | 0.035104 |  | 0.03311 |  | 0.031572 |  | 0.030198 |  | 0.028787 | 0.028026 | 0.027215 | 0.026347
| BOC Series | 420-800 | 53.6 | 9.2 | 68652 | 0.00078075 | 76280 |  | 79332 |  | 83908 |  | 88485 |  | 91536 | 93062 |  | 100690 | 0.044123 |  | 0.039711 |  | 0.038183 |  | 0.036101 |  | 0.034234 |  | 0.033093 | 0.03255 |  | 0.030084
|  | 540-1533 | 78 | 19.2 | 138000 | 0.00056522 | 153300 |  | 159432 |  | 168630 |  | 177828 |  | 183960 | 187026 |  | 202356 | 0.041629 |  | 0.037475 |  | 0.036033 |  | 0.034068 |  | 0.032306 |  | 0.031229 | 0.030717 |  | 0.02839
|  | 550-2208 | 119.9 | 23 | 198788 | 0.00060316 | 220875 |  | 229625 |  | 242875 |  | 256125 |  | 265000 | 269375 |  | 291464 | 0.036887 |  | 0.033198 |  | 0.031933 |  | 0.030191 |  | 0.028629 |  | 0.027671 | 0.027221 |  | 0.025158
| Larkin | MLT6310SA | 33.7 | 4.2 | 27900 | 0.0012079 | 31000 |  | 31620 | [5 empty] | 35650 |  |  |  | 0.055202 |  | 0.049682 |  | 0.048708 | [5 empty] | 0.043202
|  | MLT4165BA | 23.3 | 3.6 | 14850 | 0.001569 | 16500 |  | 16830 | [5 empty] | 18975
|  | MLT4250BA | 33.7 | 5.4 | 22500 | 0.0014978 | 25000 |  | 25500 | [5 empty] | 28750 |  |  |  | 0.080717 |  | 0.072645 |  | 0.071221 | [5 empty] | 0.06317
|  | LHE6450 | 27.5 | 5.2 | 40500 | 0.00067901 | 45000 |  | 46800 | [5 empty] | 51750 |  |  |  | 0.041099 |  | 0.036989 |  | 0.035566 | [5 empty] | 0.032164
|  | LHE61020 | 128.4 | 28 | 91800 | 0.0013987 | 102000 |  | 106080 | [5 empty] | 117300
|  | LHL41440 | 87.2 | 21 | 129600 | 0.00067284 | 144000 |  | 149760 | [5 empty] | 165600 |  |  |  | 0.048731 |  | 0.043858 |  | 0.042171 | [5 empty] | 0.038138
| Keeprite | 118M | 14.5 | 1.7 | [8 empty] | 17640 |  | 18000 | [11 empty] | 0.03617
|  | 245M | 26.9 | 3.4 | [8 empty] | 44100 |  | 45000 | [11 empty] | 0.028124
|  | 116L | 14.5 | 1.7 | 14900 | 0.00097315 | 16000 |  | 16300 |  | 16500 | [7 empty] | 0.042821 |  | 0.039877 |  | 0.039143 |  | 0.038669
|  | 232L | 26.9 | 1.7 | 29500 | 0.00091186 | 32000 |  | 33200 |  | 34100 | [7 empty] | 0.028789 |  | 0.02654 |  | 0.025581 |  | 0.024906
|  | 228V | 26.9 | 3.4 | 26000 | 0.0010346 | 28000 |  | 28700 |  | 29300 | [7 empty] | 0.047703 |  | 0.044296 |  | 0.043215 |  | 0.042331
[6 empty] | 0.00096142 | [11 empty] | Average | 0.044907 |  | 0.040834 |  | 0.03948 |  | 0.033173 |  | 0.030858 |  | 0.029487 |  | 0.026841
[18 empty] | Used | 0.0511 |  | 0.0463 |  | 0.0449 |  | 0.0332 |  | 0.033 |  | 0.032 |  | 0.027
Condensers |  |  |  |  | BTU Capacity @ Saturated Suction Temperatures (95F Ambient) | [13 empty] | KW-hr/BTU (18 hr runtime)
|  |  | Compressor FLA | Condenser Fan FLA
|  | Model | 230/3 | 230/3 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35
| RAE | DS05H4 | 22.3 | 2.2 |  |  |  |  | 25180 |  | 31413 |  | 39012 |  | 47822 | 52666 | 57711 | [5 empty] | 0.22379 |  | 0.17938 |  | 0.14444 |  | 0.11783 | 0.107 | 0.097642
|  | DS10H4 | 43.6 | 4.4 |  |  |  |  | 55291 |  | 66887 |  | 81209 |  | 98341 | 107808 | 117893 | [5 empty] | 0.10192 |  | 0.084247 |  | 0.069389 |  | 0.057301 | 0.052269 | 0.047798
|  | DS03L4 | 16.8 | 2.2 | 14255 |  | 18981 |  | 24500 |  | 30768 | [7 empty] | 0.3953 |  | 0.29688 |  | 0.23 |  | 0.18314
|  | DS11L4 | 45.2 | 4.6 | 42747 |  | 55948 |  | 70909 |  | 87701 | [7 empty] | 0.13182 |  | 0.10072 |  | 0.079468 |  | 0.064252
| Bohn | BD*0500M6 | 20 | 2.7 |  |  |  |  | 19560 |  | 25330 |  |  | 32220 | 39280 |  | 46880 | [5 empty] | 0.28809 |  | 0.22246 |  |  | 0.17489 | 0.14346 |  | 0.1202
|  | BD*1000M6 | 39 | 5.4 |  |  |  |  | 50180 |  | 63630 |  | 79060 |  | 93930 |  | 109930 | [5 empty] | 0.1123 |  | 0.088559 |  | 0.071275 |  | 0.059991 |  | 0.05126
|  | BD*1500M6 | 53.5 | 8.8 |  |  |  |  | 69470 |  | 87380 |  | 108240 |  | 128610 |  | 150350
|  | BD*0400L6 | 23.6 | 2.7 | 17400 |  | 23140 |  | 29620 |  | 36470 | [7 empty] | 0.32385 |  | 0.24352 |  | 0.19024 |  | 0.15451
|  | BD*1200L6 | 40.9 | 8.8 | 41970 |  | 55650 |  | 70880 |  | 86720 | [7 empty] | 0.13426 |  | 0.10126 |  | 0.079501 |  | 0.064979
|  | BD*2200L6 | 57.7 | 8.8 | 64540 |  | 83410 |  | 103010 |  | 122150
| Keeprite | KEZA010M6 | 10 | 0.5 |  |  |  |  | 5900 |  | 7400 |  | 9100 |  | 11000 |  | 14200
|  | KEZA025M6 | 10 | 1.1 |  |  |  |  | 11500 |  | 14200 |  | 17300 |  | 20800 |  | 24600 | [5 empty] | 0.49 |  | 0.39683 |  | 0.32572 |  | 0.27091 |  | 0.22907
|  | KEZA035M6 | 13.9 | 2.1 |  |  |  |  | 16300 |  | 20200 |  | 24700 |  | 29700 |  | 35300 | [5 empty] | 0.34571 |  | 0.27896 |  | 0.22814 |  | 0.18973 |  | 0.15963
|  | KEZA060L6 | 23.9 | 2.1 | 18300 |  | 22800 |  | 28000 |  | 33900 | [7 empty] | 0.30792 |  | 0.24715 |  | 0.20125 |  | 0.16622
|  | KEZA150L6 | 55 | 4.2 | 42200 |  | 52700 |  | 64800 |  | 78400 | [7 empty] | 0.13353 |  | 0.10693 |  | 0.08696 |  | 0.071875
[18 empty] | Average | 0.23778 |  | 0.2222 |  | 0.20243 |  | 0.16295 |  | 0.16779 |  | 0.13987 |  | 0.1176
[18 empty] | Used | 0.2378 |  | 0.23 |  | 0.225 |  | 0.22 |  | 0.2158 |  | 0.1744 |  | 0.142
Total System KW-Hr used for 18hr runtime, 4 defrost per day, 20 min
[19 empty] | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30
[18 empty] | Used | 0.00031779 | 0.00031086 | 0.00030393 | 0.00030041 | 0.00029689 | 0.00028771 | 0.00027852 | 0.0002761 | 0.00027368 | 0.00025036 | 0.00022704 | 0.00020647 | 0.0001859

## Energy Calc Sheet #2 (hidden)
|  |  | Defrost Heater Amps | Total Fan Motor Amps | BTU Capacity @ Saturated Suction Temperatures | [13 empty] | W-hr/BTU(18 hr runtime, 4 defrost per day, 20 min defrost)
|  | Model | 230/3 | 230/3 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35
Electric Defrost | BOC Series | 420-800 | 53.6 | 9.2 | 68652 |  | 76280 |  | 79332 |  | 83908 |  | 88485 |  | 91536 | 93062 |  | 100690 | 0.066746 | 0.063408 | 0.060071 | 0.058916 | 0.05776 | 0.056185 | 0.05461 | 0.053198 | 0.051785 | 0.050922 | 0.050059 | 0.049238 | 0.047373 | 0.045508
Air Defrost | BOC Series | 420-800 | 0 | 9.2 | 68652 |  | 76280 |  | 79332 |  | 83908 |  | 88485 |  | 91536 | 93062 |  | 100690 | 0.057935 | 0.055038 | 0.052141 | 0.051138 | 0.050135 | 0.048768 | 0.047401 | 0.046175 | 0.044949 | 0.0442 | 0.043451 | 0.042739 | 0.04112 | 0.039501
|  |  | Compressor | Fan
Low Temp | BD*0400L6 |  | 23.6 | 2.7 | 17400 |  | 23140 |  | 29620 |  | 36470 | [7 empty] | 0.49009 | 0.4293 | 0.36852 | 0.32821 | 0.2879 | 0.26086 | 0.23382
Med Temp | DS05H4 |  | 22.3 | 2.2 |  |  |  |  | 25180 |  | 31413 |  | 39012 |  | 47822 | 52666 | 57711 | [5 empty] | 0.31548 | 0.28418 | 0.25289 | 0.22826 | 0.20363 | 0.18487 | 0.16611 | 0.15084 | 0.13765 | 0.12446
[18 empty] | Average | 0.49009 | 0.4293 | 0.36852 | 0.32821 | 0.30169 | 0.27252 | 0.24335 | 0.22826 | 0.20363 | 0.18487 | 0.16611 | 0.15084 | 0.13765 | 0.12446
Assumptions
| These units are the best average units on the KW-Calc page | [16 empty] | Compressor | Electric | Air
| Electric Defrost has 4 20 min defrost per day | [15 empty] | -40 | 0.67282 | 0.080762 | 0.070101
| Air Defrost has the evap fans running 24 hrs per day | [15 empty] | -35 | 0.60596 | 0.077091 | 0.066915
| 18 hr pull down used for Air and Electric Defrost units | [15 empty] | -30 | 0.5391 | 0.07342 | 0.063728
| Used same Evap coil data for Electric Defrost unit and did not use heaters to calculate Air Defrost | [15 empty] | -25 | 0.47223 | 0.069749 | 0.060542
| Averaged W-hr/Btu factor for data point not available | [15 empty] | -20 | 0.40537 | 0.066078 | 0.057355
| Added 10% penalty on efficiency factor to reflect used equipment | [15 empty] | -15 | 0.36103 | 0.064807 | 0.056252
[17 empty] | -10 | 0.33186 | 0.063536 | 0.055149
[17 empty] | -5 | 0.29977 | 0.061804 | 0.053645
[17 empty] | 0 | 0.26769 | 0.060071 | 0.052141
[17 empty] | 5 | 0.25108 | 0.058517 | 0.050793
[17 empty] | 10 | 0.22399 | 0.056964 | 0.049444
[17 empty] | 15 | 0.20336 | 0.056014 | 0.04862
[17 empty] | 20 | 0.18272 | 0.055065 | 0.047796
[17 empty] | 25 | 0.16592 | 0.054162 | 0.047012
[17 empty] | 30 | 0.15141 | 0.052111 | 0.045232
[17 empty] | 35 | 0.13691 | 0.050059 | 0.043451